## 1
ATTACHMENT INFORMATION SHEET - REVISION 6/14/2017 | [7 empty] | Notes:
[8 empty] | 1) Enter all measurements in decimal format (ie 15 ft 6" = 15.5) |  |  |  |  | Decimal Conversion:
Licensee |  | MCIMetro |  | Pole Total | 64 |  |  | 2) Lowest power at pole may be neutral, secondary, top of terminal riser, bottom of drip loops, etc. |  |  |  |  | 0" = .00 | 4" = .33 | 8" = .67
Licensee # |  | Horton Spoke 3 |  | # of New | 30 |  |  | 3) For Power Equipment, note transformers, capacitor banks, switches, etc. |  |  |  |  | 1" = .08 | 5" = .42 | 9" = .75
Location |  | St Paul, MN |  | # of Overlash | 0 | [7 empty] | 2" = .17 | 6" = .50 | 10" = .83
PPA # |  |  |  | Attachment Total | 30 |  |  | Please refer to the Appendix on "Communications Attachments to Xcel Energy Distribution Facilities" |  |  |  |  | 3" = .25 | 7" = .58 | 11" = .92 | [20 empty] | For Xcel Energy Use Only
[8 empty] | for specific clearance requirements. A copy of the Appendix can be obtained by calling (651) 229-2500. | [7 empty] | Highest Existing Communications Pass / Fail Equipment Clearance |  |  |  | Proposed Communications Pass / Fail Equipment Clearance Requirements | [5 empty] | Pass / Fail Vertical Clearance
[5 empty] | Power Pole & Equipment | [10 empty] | 48" from power cable | 12" from street light bracket / drip loop | 12" clearance from Communications (2) | 19.5' at Pole Above Surface | 48" from power cable | 12" from street light bracket / drip loop | 30" mid-span power cable clearance | 12" clearance from Communications (1) | 12" clearance from Communications (2) | 12" clearance from Communications (3) | 19.5' at Pole Above Surface | 15.5' at Mid-span Above Surface (Must meet Sht J-6 min. and local ord.) | Pole Loading Information | [6 empty] | Proposed Modifications / Make-Ready Necessary to Allow for Attachment
[9 empty] | Existing Attachment Height Information |  |  |  |  | Proposed Attachment Information | [13 empty] | Span Length | Cable Diameter | Cable Weight | Structure Type (Tangent, Dead-End, Angle, etc.) | Current % Loading | Proposed % Loading | Guy / Anchor Required? |  | Approved / Denied / Approved with Conditions | Make Ready Required / Comments | Approved Attachment Height | Guy/ Anchor Required? | Post Inspection Height | Pass/ Fail
Pole No. (on Map) | New (N) or Overlash (O) | Xcel Energy GIS Pole ID | Latitude | Longitude | Pole Ht/ Class | Power Equipment on Pole | Lowest Power at Pole | Lowest Power Cable at Mid-span | Street Light Bracket / Drip Loop (Lowest) | Highest Existing Communic. At Pole (1) | Existing Communic. At Pole (2) | Existing Communic. At Pole (3) | # of Existing Risers | Proposed Attachment Height for New Cable | Proposed Mid-span Cable Height (Must meet Sht J-6 min. and local ord.)
| Overlash (O) or New (N) | [26 empty] | Pole Loading Current | Pole Loading Current | Pole Loading Current | Pole Loading Current | Pole Loading Current | Pole Loading Current | Pole Loading Current |  | Pole Loading Current | Pole Loading Current | Pole Loading Current |  | Pole Loading Current | Pole Loading Current
24 | N | 37742593 |  |  | 50-3 |  | 36 | 32.33 |  | 26.92 | 26.17 |  |  | 25.17 | 23 | PASS |  | 9 | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 104 | 1.03 | 0.37 | Dead-End | 24.4 | 25.7% | Yes
25 | N | 37740535 |  |  | 50-3 |  | 33 | 31.25 |  | 23.75 | 22.92 |  |  | 21.92 | 23.42 | PASS |  | 9.96 | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 144 | 1.03 | 0.37 | Tangent | 27.9 | 30.6% | No
26 | N | 37740529 |  |  | 50-3 | XFMR | 31.42 | 30.75 |  | 27.83 | 27.08 |  |  | 26.08 | 22.33 | 43.08 |  | 9 | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 115 | 1.03 | 0.37 | Tangent | 28.5 | 32.6% | No
27 | N | 37740523 |  |  | 50-3 |  | 33.83 | 29.67 |  | 23.75 | 22.58 |  |  | 21.58 | 20.17 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 148 | 1.03 | 0.37 | Junction | 42.8 | 45.9% | No
28 | N | 37740517 |  |  | 40-5 |  | 29.42 | 26.92 |  | 24.92 | 23.83 |  |  | 22.83 | 19 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 201 | 1.03 | 0.37 | Tangent | 48.8 | 58.1% | No
29 | N | 37740511 |  |  | 40-5 |  | 30.42 | 21.92 |  | 24.17 | 23.25 |  |  | 22.25 | 16 | PASS |  | 11.04 | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 235 | 1.03 | 0.37 | Tangent | 62.4 | 73.8% | No | A1 Re-sag span South. CTL Re-sag span South.
30 | N | 37740415 |  |  | 40-5 |  | 24.92 | 21.33 |  | 21.42 | 20.42 |  |  | 19.42 | 16.08 | 42 |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | 19.42 | PASS | 168 | 1.03 | 0.37 | Tangent | 50.2 | 59.5% | No
31 | N | 37740409 |  |  | 40-4 |  | 27.33 | 26.92 |  | 22.42 | 21 |  |  | 20 | 19.33 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 107 | 1.03 | 0.37 | Junction | 80.2 | 80.3% | Yes
32 | N | 37740421 | P-P Guy |  | 40-5 | XFMR, STL | 24.92 | 25.75 | 22.08 | 19 | 17.42 |  |  | 12.5 |  | PASS | PASS | PASS | 19 | PASS | PASS |  | PASS | PASS |  | 12.5 |  | 80 | 1.03 | 0.37 | Tangent | 48 | 51.1% | Yes
33 | N | 37740400 | CTL Pole |  | 45-4 | XFMR, STL, Riser | 27.58 | 28.17 | 23.75 | 22.08 | 20.67 |  | 1 | 19.67 | 17.25 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS |  | PASS | PASS | 111 | 1.03 | 0.37 | Tangent | 46.2 | 49.4% | No
34 | N | 37761638 | CTL Pole |  | 45-4 | STL, Riser | 30.08 | 27.67 | 29.5 | 20.17 | 18.67 |  | 1 | 18.67 | 17.33 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS | 0 |  | 18.67 | PASS | 91 | 1.03 | 0.37 | Tangent | 45 | 48.3% | No | A1 Raise 12" to 21'2". This will require a splice in the COAX riser. CTL Raise 18" to 20'2"
35 | N | 37761626 | CTL Pole |  | 40-4 | XFMR | 28 | 26.25 |  | 22.33 | 20.33 |  | 1 | 19.33 | 19.33 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | 19.33 | PASS | 65 | 1.03 | 0.37 | Tangent | 36.7 | 39.5% | No | CTL Rotate terminal 90 degrees.
36 | N | 37761620 |  |  | 45-3 |  | 26.67 | 26.5 |  | 23 | 21.75 |  |  | 20.75 | 19.58 | 44.04 |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 109 | 1.03 | 0.37 | Junction | 45 | 46.1% | No
37 | N | 37761632 | CTL Pole |  | 40-4 | STL | 27.42 | 28.08 | 26.33 | 21.83 | 20.08 |  |  | 19.08 | 16.5 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS |  | 19.08 | PASS | 98 | 1.03 | 0.37 | Tangent | 43 | 46.4% | No | CTL Rotate terminal 90 degrees.
38 | N | 37762661 |  |  | 45-5 | XFMR | 31.83 | 29.42 |  | 19.17 | 17.58 |  |  | 16.58 | 16.75 | PASS |  | PASS | 19.17 | PASS |  | PASS | PASS | PASS |  | 16.58 | PASS | 51 | 1.03 | 0.37 | Tangent | 41.3 | 43.9% | No
39 | N | 37762667 | CTL Pole |  | 40-5 | Riser | 24.67 | 26.25 |  | 20.42 | 18.58 |  | 1 | 17.58 | 17.58 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | 17.58 | PASS | 103 | 1.03 | 0.37 | Tangent | 51 | 54.3% | No
40 | N | 37756598 | CTL Pole |  | 40-5 | STL, Riser | 27.25 | 24.83 | 24.25 | 21.58 | 20 |  | 1 | 19 | 18.33 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS |  | 19 | PASS | 49 | 1.03 | 0.37 | Tangent | 42.7 | 44.8% | No
41 | N | 37756703 |  |  | 45-3 | PTS, Riser | 23.25 | 22.5 |  | 22.67 | 19.08 |  | 1 | 18.08 | 16 | 6.96 |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | 18.08 | PASS | 136 | 1.03 | 0.37 | Tangent | 29.5 | 31.4% | No | A1 Lower 33" to 19'11" and re-sag. CTL Re-sag span west.
42 | N | 37756679 | CTL Pole |  | 45-3 | STL | 22.25 | 19.42 | 25.83 | 17.08 | 15.25 |  |  | 17.08 | 15.92 | PASS | PASS | PASS | 17.08 | PASS | PASS | PASS | 0 | PASS |  | 17.08 | PASS | 74 | 1.03 | 0.37 | Tangent | 33.3 | 36.7% | No | Re-Frame and raise cabled secondary to 24'10". Secondary is wrapped around the face of pole. A1 Raise 24" to 19'1" CTL Raise 34" to 18'1"
43 | N | 37756496 | CTL Pole |  | 45-4 | XFMR, STL | 23.08 | 23.75 | 21.42 | 18.08 | 16.67 |  |  | 15.67 | 15.75 | PASS | PASS | PASS | 18.08 | PASS | PASS | PASS | PASS | PASS |  | 15.67 | PASS | 97 | 1.03 | 0.37 | Tangent | 46.1 | 46.7% | No
44 | N | 37756481 |  |  | 40-3 | XFMR, STL | 25.33 | 23.83 | 23.83 | 20.5 | 19 |  |  | 18 | 16.08 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS |  | 18 | PASS | 96 | 1.03 | 0.37 | Tangent | 47.1 | 50% | No | CTL Rotate terminal 90 degrees.
45 | N | 37756487 |  |  | 40-3 | Riser | 24.42 |  |  | 22 |  |  | 1 | 20 |  | 29.04 |  |  | PASS | PASS |  |  | PASS |  |  | PASS |  |  | 1.03 | 0.37 | Dead-End | 18.8 | 19.7% | Yes | A1 Lower 12" to 21'0"
46 | N | 37770951 | CTL Pole |  | 45-3 | XFMR, Riser | 25.67 | 24 |  | 20.75 | 18.5 |  | 2 | 21.75 | 19.42 | PASS |  | PASS | PASS | 47.04 |  | PASS | PASS | PASS |  | PASS | PASS | 123 | 1.03 | 0.37 | Dead-End | 43.9 | 43.8% | Yes
47 | N | 37770957 | CTL Pole |  | 40-4 |  | 28.58 | 25.33 |  | 20.17 | 18.25 |  |  | 21.17 | 20.33 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 76 | 1.03 | 0.37 | Tangent | 43.6 | 47.5% | No
48 | N | NT-1 | CTL Pole |  | 35-5 |  | 24 | 23.58 |  | 19.58 | 18.08 |  |  | 20.58 | 20.5 | PASS |  | PASS | PASS | 41.04 |  | PASS | PASS | PASS |  | PASS | PASS | 164 | 1.03 | 0.37 | Tangent | 39.3 | 46.3% | No
49 | N | 37770963 | CTL Pole |  | 40-4 | XFMR, STL | 22.67 | 21.17 | 21.08 | 18.17 | 16.33 |  | 1 | 19.17 | 18.83 | PASS | PASS | PASS | 18.17 | 42 | PASS | 28.08 | PASS | PASS |  | 19.17 | PASS | 120 | 1.03 | 0.37 | Tangent | 42.2 | 47.3% | No
50 | N | 37770969 | CTL Pole |  | 40-5 | Riser | 25.33 | 27.25 |  | 19.5 | 18.17 |  | 1 | 20.5 | 20.33 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 79 | 1.03 | 0.37 | Tangent | 34 | 37.8% | No
51 | N | 37770975 | CTL Pole |  | 40-5 | XFMR | 29.67 | 25.92 |  | 19.83 | 18.08 | 17.75 |  | 20.83 | 20.33 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS | PASS | PASS | PASS | 81 | 1.03 | 0.37 | Tangent | 29.4 | 32.2% | No
52 | N | 37770981 | CTL Pole |  | 35-5 |  | 24.92 | 24.42 |  | 19.17 | 17.83 |  |  | 20.17 | 19.58 | PASS |  | PASS | 19.17 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 81 | 1.03 | 0.37 | Tangent | 32.3 | 36.7% | No
53 | N | 37770987 | CTL Pole |  | 35-5 |  | 24.42 | 26.25 |  | 18.08 | 16 |  |  | 19.08 | 19.17 | PASS |  | PASS | 18.08 | PASS |  | PASS | PASS | PASS |  | 19.08 | PASS | 83 | 1.03 | 0.37 | Tangent | 42.4 | 46.7% | No
54 | N | 37771251 | CTL Pole |  | 40-5 | Riser | 28.42 | 23.92 |  | 18.75 | 16.83 |  | 1 | 19.75 | 19 | PASS |  | PASS | 18.75 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 109 | 1.03 | 0.37 | Tangent | 36.5 | 40.8% | No
55 | N | 37770993 | CTL Pole |  | 40-3 | XFMR, STL | 23.75 | 25.67 | 20.33 | 19.67 | 18.5 |  |  | 19.67 | 20.08 | PASS | 7.92 | PASS | PASS | PASS | 7.92 | PASS | 0 | PASS |  | PASS | PASS | 118 | 1.03 | 0.37 | Tangent | 31 | 34.2% | No | STL Bond to ground, place split duct over STL drip loops. A1 Lower 14" to 18'6" CTL Lower 6" TO 17' 6"
56 | N | 37770999 | CTL Pole |  | 45-4 | Riser | 29 | 23.5 |  | 20.67 | 19.42 | 18.58 | 1 | 21.67 | 19.83 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS | PASS | PASS | PASS | 123 | 1.03 | 0.37 | Tangent | 39.1 | 43.4% | No
57 | N | 37752188 | CTL Pole |  | 40-4 | XFMR | 23.75 | 24.92 |  | 20.33 | 19.17 | 18.17 |  | 20.33 | 20.83 | 41.04 |  | PASS | PASS | 41.04 |  | PASS | 0 | PASS | PASS | PASS | PASS | 88 | 1.03 | 0.37 | Tangent | 32.5 | 36.3% | No | A1 Lower 14" to 19'2" CTL Lower top attachment to 18'2"
58 | N | 37752194 | CTL Pole |  | 40-5 |  | 29.67 | 29.17 |  | 21.83 | 19.75 |  |  | 22.83 | 23.25 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 71 | 1.03 | 0.37 | Tangent | 22.1 | 24.6% | No
59 | N | 37752200 | CTL Pole |  | 40-5 | XFMR | 28.83 | 26.75 |  | 20.92 | 19 |  |  | 23 | 20.83 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 150 | 1.03 | 0.37 | Tangent | 46.5 | 52.3% | No
60 | N | 37752287 | CTL Pole |  | 40-5 |  | 29.75 | 25.5 |  | 21.08 | 19.42 |  | 1 | 22.08 | 20.08 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 80 | 1.03 | 0.37 | Tangent | 45.2 | 51.1% | No
61 | N | 37752866 | CTL Pole |  | 40-5 | XFMR, STL, Riser | 23 | 22.33 | 22.17 | 19.5 | 18.5 |  | 1 | 19.5 | 19.33 | 42 | PASS | PASS | PASS | 42 | PASS | PASS | 0 | PASS |  | PASS | PASS | 120 | 1.03 | 0.37 | Tangent | 53.1 | 57.1% | No | A1 Lower 12" to 18'6" CTL Lower 12" to 17'6"
62 | N | 37752293 | CTL Pole |  | 40-4 | XFMR | 28.17 | 28.33 |  | 20.67 | 18.75 |  |  | 21.67 | 21.17 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 83 | 1.03 | 0.37 | Tangent | 45.7 | 49.8% | No
63 | N | 37752299 | CTL Pole |  | 45-3 | Riser, STL | 30.42 | 27.83 | 26.83 | 20.75 | 18.75 |  | 1 | 21.75 | 20.25 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS |  | PASS | PASS | 82 | 1.03 | 0.37 | Tangent | 57.2 | 59.7% | No
64 | N | 37752305 | CTL Pole |  | 40-5 | XFMR, Riser | 21.67 | 24.75 |  | 20.58 | 18.67 |  | 2 | 19.67 | 18.42 | 13.08 |  | PASS | PASS | 24 |  | PASS | 10.92 | PASS |  | PASS | PASS | 108 | 1.03 | 0.37 | Tangent | 53 | 56.7% | No | Place U-Guard extensions over both power riser- Extend to 23'0" A1 Lower 23" to 18'8" CTL Lower 12" to 17'8"
65 | N | 37752311 | CTL Pole |  | 40-4 | XFMR, STL | 29.42 | 26.5 | 27 | 21.33 | 19.5 |  |  | 21.33 | 20.67 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | 0 | PASS |  | PASS | PASS | 63 | 1.03 | 0.37 | Tangent | 38.3 | 41.2% | No | A1 Lower 11" to 20'5"
66 | N | 37752317 |  |  | 40-4 |  | 23.33 | 26.75 |  | 21.33 | 19 |  |  | 21.33 | 22.67 | 24 |  | PASS | PASS | 24 |  | PASS | 0 | PASS |  | PASS | PASS | 71 | 1.03 | 0.37 | Junction | 49.8 | 50.5% | No | Attach bottom secondary to existing 3 spool bracket. A1 Lower 12" to 20'4"
67 | N | 37752335 |  |  | 40-5 |  | 28.83 | 25.67 |  | 22 | 20 |  |  | 23 | 21.08 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 120 | 1.03 | 0.37 | Tangent | 45.9 | 51% | No
68 | N | 37752347 |  |  | 40-5 | STL | 27.33 | 24.25 | 25.42 | 21.5 | 19.92 |  |  | 22.5 | 22 | PASS | PASS | PASS | PASS | PASS | PASS | 27 | PASS | PASS |  | PASS | PASS | 123 | 1.03 | 0.37 | Tangent | 69.1 | 72.8% | No | Remove abandoned secondary between poles.
69 | N | 37752353 |  |  | 45-4 | XFMR, Riser | 27.67 | 28 |  | 21.83 | 19.75 |  | 1 | 22.83 | 22.08 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 121 | 1.03 | 0.37 | Tangent | 61.2 | 64.5% | No
70 | N | 37752359 |  |  | 45-4 |  | 33.42 | 25.33 |  | 22.42 | 20.58 |  |  | 23.42 | 20.33 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 141 | 1.03 | 0.37 | Tangent | 53.5 | 58.6% | No
71 | N | 37752839 |  |  | 45-3 | XFMR, STL, Riser | 25.5 | 25.92 | 22.67 | 19 | 17.5 |  | 1 | 20 | 19.67 | PASS | PASS | PASS | 19 | PASS | PASS | PASS | PASS | PASS |  | PASS | PASS | 99 | 1.03 | 0.37 | Tangent | 65.6 | 67.4% | No
72 | N | 37752365 |  |  | 50-3 |  | 28.67 | 26.5 |  | 22.17 | 21.25 | 19.92 | 1 | 23.17 | 20.42 | PASS |  | 11.04 | PASS | PASS |  | PASS | PASS | PASS | PASS | PASS | PASS | 119 | 1.03 | 0.37 | Junction | 50.3 | 50.4% | No
73 | N | 37752563 |  |  | 45-3 | XFMR | 23.25 | 22 |  | 20.58 | 18.58 |  | 2 | 19.58 | 19.25 | 32.04 |  | PASS | PASS | 44.04 |  | PASS | PASS | PASS |  | PASS | PASS | 138 | 1.03 | 0.37 | Tangent | 55 | 59.1% | No | A1 Lower 24" to 18'7" and re-sag span West. CTL Lower 12" to 17'7"
74 | N | 37752629 | CTL Pole |  | 45-4 | XFMR, STL | 28.25 | 24.75 | 25.75 | 23.83 | 22.33 |  |  | 22.33 | 19.42 | PASS | PASS | PASS | PASS | PASS | PASS | PASS | PASS | 0 |  | PASS | PASS | 127 | 1.03 | 0.37 | Tangent | 80.2 | 83.3% | No | A1 Lower 30" to 21'4" CTL Lower 24" to 20'4"
75 | N | 37752635 |  |  | 45-3 | STL, Riser | 24.33 | 23.25 | 26.17 | 20.08 | 18.58 |  | 1 | 21.08 | 18.67 | PASS | PASS | PASS | PASS | 39 | PASS | PASS | PASS | PASS |  | PASS | PASS | 123 | 1.03 | 0.37 | Tangent | 39.6 | 42.8% | No | A1 Complete transfer to new pole. Extend power supply weather head.
76 | N | 37752641 |  |  | 40-5 | XFMR,STL | 23.5 | 20.67 | 22 | 16.75 | 16 |  |  | 17.75 | 18.17 | PASS | PASS | 9 | 16.75 | PASS | PASS | PASS | PASS | PASS |  | 17.75 | PASS | 127 | 1.03 | 0.37 | Tangent | 78.6 | 82.5% | No
77 | N | 37752647 | CTL Pole |  | 40-5 | XFMR | 22.75 | 23.58 |  | 19.17 | 17.92 |  |  | 19.17 | 18.75 | 42.96 |  | PASS | 19.17 | 42.96 |  | PASS | 0 | PASS |  | 19.17 | PASS | 72 | 1.03 | 0.37 | Tangent | 58.8 | 62.8% | No | A1 Lower 15" to 17'11" CTL Lower 12" to 16'11"
78 | N | 37752653 | CTL Pole |  | 40-5 |  | 25.42 | 25.67 |  | 17.83 | 16.5 |  |  | 18.83 | 20 | PASS |  | PASS | 17.83 | PASS |  | PASS | PASS | PASS |  | 18.83 | PASS | 39 | 1.03 | 0.37 | Tangent | 58.3 | 59.1% | No
79 | N | 337045108 |  |  | 45-3 | Cap Bank, Riser | 23.92 | 24.58 |  | 18.83 | 17.92 |  | 1 | 19.83 | 21.5 | PASS |  | 10.92 | 18.83 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 126 | 1.03 | 0.37 | Tangent | 27.7 | 30% | No
80 | N | 37752665 CTL |  |  | 45-3 | Riser, STL | 24.67 | 20.92 | 24.75 | 21.83 | 21 | 20.75 | 1 | 21 | 17.67 | 34.08 | PASS | 9.96 | PASS | 44.04 | PASS | PASS | 9.96 | 0 | 3 | PASS | PASS | 123 | 1.03 | 0.37 | Tangent | 47.7 | 49.4% | No | A1 Lower 22" to 20'0" CTL Lower to 19'0"
81 | N | 37752680 |  |  | 45-4 | XFMR | 23.33 | 25.25 |  | 17.83 | 16.92 |  |  | 18.83 | 19.42 | PASS |  | 10.92 | 17.83 | PASS |  | PASS | PASS | PASS |  | 18.83 | PASS | 108 | 1.03 | 0.37 | Tangent | 52.3 | 56% | No
82 | N | 33752713 | CTL Pole |  | 45-4 |  | 30.5 | 25 |  | 18.83 | 17.33 |  | 1 | 20.83 | 20.17 | PASS |  | PASS | 18.83 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 134 | 1.03 | 0.37 | Tangent | 54.1 | 57.7% | No
83 | N | 33753274 | CTL Pole |  | 40-5 |  | 26.75 | 24.5 |  | 20.33 | 17.83 |  |  | 21.33 | 20.33 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 42 | 1.03 | 0.37 | Tangent | 72.6 | 75.3% | No
84 | N | 390933217 |  |  | 45-3 | XFMR | 23.17 | 21.33 |  | 19.17 | 18.5 |  |  | 19.5 | 18.83 | PASS |  | 8.04 | 19.17 | 44.04 |  | PASS | 3.96 | PASS |  | PASS | PASS | 77 | 1.03 | 0.37 | Tangent | 27.7 | 30.9% | No | A1 Frame to pole at 18'6" CTL Lower 12" to 17'6"
85 | N | 37753280 |  |  | 40-5 | XFMR | 22.83 | 21.25 |  | 19.17 | 18.25 | 17.33 |  | 19.17 | 18.75 | 43.92 |  | 11.04 | 19.17 | 43.92 |  | PASS | 0 | 11.04 | PASS | 19.17 | PASS | 111 | 1.03 | 0.37 | Tangent | 50.1 | 54.1% | No | A1 Lower 11" to 18'3" CTL Lower top attachment to single point at 17'4"
86 | N | 37753292 |  |  | 45-3 | Riser | 25.92 | 24 |  | 19.17 | 18.17 |  | 1 | 20.17 | 21 | PASS |  | PASS | 19.17 | PASS |  | PASS | PASS | PASS |  | PASS | PASS | 86 | 1.03 | 0.37 | Tangent | 35.6 | 38% | No
87 | N | 37753310 |  |  | 50-3 | XFMR | 25.67 | 22.67 |  | 19.83 | 18.83 |  | 2 | 21 |  | PASS |  | PASS | PASS | PASS |  |  | PASS | PASS |  | PASS |  | 126 | 1.03 | 0.37 | Dead-End | 50.5 | 55.8% | Yes
Note on A20: Michels: